STAFF'S STATUS REPORT

Case No. GS-2004-0257

BACKGROUND:

A natural gas incident occurred in Springfield, Missouri at the Ozark Empire Fairgrounds on June 18, 2003, in which natural gas leaking from a plastic pipe resulted in an explosion of the Frisco Building.  An employee of the Ozark Empire Fair was fatally injured.  The leak in the plastic pipe was the result of a rock impingement that caused the pipe to fail, resulting in natural gas escaping into the lower level of the Frisco Building.  The Energy Department–Gas Safety/Engineering Staff (Staff) conducted a formal investigation of the incident and filed its Gas Incident Report (Case No. GS-2004-0040) on December 16, 2003.

During the incident investigation, records provided to the Staff by City Utilities indicated other instances of brittle-like cracking failures on plastic pipe due to rock impingement.   Based upon that information, Staff recommended that the Commission establish a separate case (Case No. GS-2004-0257) for the purpose of examining and evaluating City Utilities’ plastic pipe failures, leak survey techniques, installation and backfill procedures, replacement criteria, and adequacy of their program activities.

The Commission opened this case on December 30, 2003, as an investigatory case to receive information and conduct an investigation into the failure mechanisms of both plastic mains and service lines used by City Utilities of Springfield.  On June 16, 2004, Staff filed its report in Case No. GS-2004-0257, which summarized Staff’s investigation into City Utilities’ plastic mains and service lines.  The Report contained eight recommendations for City Utilities to follow and requested that the Commission issue an order directing City Utilities to file a response regarding the recommendations within 60 days of the filing of Staff’s report.  On August 16, 2004, City Utilities filed its response to Staff’s recommendations.  On September 10, 2004, the Commission issued an order for Staff to file a Status Report, no later than October 12, 2004, on the ongoing nature of the monitoring, evaluation, and replacement of the plastic pipe in City Utilities’ system.  In response, the Staff submits the following information to address this Commission Order.

REPORT OVERVIEW:

The following Status Report pertains to Staff’s on-going investigation into plastic pipe leaks due to rock impingement and the plastic pipe replacement program.  For purposes of this report, Staff will provide an analysis of City Utilities’ August 16, 2004 response to the eight recommendations contained in Staff’s report filed June 16, 2004, and a Status Report on actions that have been taken.

##### STAFF STATUS REPORT

Based upon its investigation into City Utilities’ plastic pipe failures due to rock impingement (GS-2004-0257), the Staff recommended eight actions City Utilities should undertake in development of a comprehensive City Utilities’ plastic pipe replacement program.  Those recommendations were as follows.

- The Staff recommended that City Utilities continue the current practice of voluntarily replacing all of the plastic mains that have been included within a list of rock impingement leaks.  The details of the replacement priorities and amounts per year (number of miles a year to be replaced) will have to be worked out at a later date.

- Regarding a separate list of plastic pipe leaks from 1983-2003, the Staff

recommended that all plastic services that had a portion (partial replacement) of the service line replaced due to material failure, aged/worn component, natural causes, or other, be replaced from main to the meter.  The replacement priority must be based on leak/failure history, pipe diameter, pressure district, pipe-loading conditions (under vent restrictive surfaces where vehicle traffic may cross), age of plastic pipe, etc.  The specific priorities and replacement amount per year will also have to be determined at a later date.

- The Staff recommended that City Utilities review the current Plastic Pipe Failure Report and develop instructions and guidelines for filling out this Report to be used for field applications.  The Staff also recommended that a section be added to the Report just for “rock impingement”.  A lot of different terminologies have been used in the past to describe plastic piping failures due to rock impingement.  For instance, the primary cause of documented past leaks/failures on plastic piping typically included four different categories of “aged/worn component”, “material failure”, “natural causes”, and “other”.  The leaks on this list were confirmed to be plastic pipe failures that involved rock impingement.  Due to this inconsistency used in the field for describing leak causes, the Staff believed that another leak cause category should be added for the special cases where a rock was found to be in direct contact with the plastic wall of the pipe that subsequently caused a brittle-like failure.  This leak cause category should be defined as “rock impingement”.  If some other type of foreign object is found lying against plastic piping that appears to have caused the failure, the object description could be included within a comment section beneath “rock impingement”.

- The Staff recommended that once City Utilities has reviewed the Plastic Pipe Failure Report and has implemented the desired changes, training should be conducted for all field personnel that may be involved in leak repair.  The training should emphasize that whenever a failure has occurred due to rock impingement, the primary leak cause must be recorded as “rock impingement” and the backfill conditions surrounding the pipe must also be documented within the Plastic Pipe Failure Report.

- The Staff recommended that City Utilities develop an on-going field monitoring program to identify other possible areas that may be susceptible to rock impingement.  In particular, whenever a section of plastic main or service line is exposed for any reason other than an underground leak (repairs, making service taps, exposed excavations, scheduled pipeline relocation projects, etc.) the backfill conditions surrounding the plastic piping should be evaluated and documented.  If the backfill condition surrounding the plastic piping contains rocks, or other debris, in direct contact with the piping that could potentially cause a brittle-like failure, the bedding surrounding the plastic piping in that area should be replaced with AG limestone, sand, or other suitable material that is free from rocks.  The excavation in the open trench should also be extended in both directions along the main or service line until suitable backfill conditions are encountered.

The Staff believed that an Exposed Pipeline Condition Report could be revised/edited to accommodate the above information or a new form (e.g. Backfill Condition Report) could be developed.  The information acquired from either the Exposed Pipeline Condition Report or Backfill Condition Report could then entered into a separate database file for tracking these observations.

- The Staff recommended that AG limestone or sand free of rocks be used as

bedding material around the plastic piping for all new plastic service line installations that involve open trenches.  This would include any new installations for business, commercial, and residential areas, whenever the open trench style of installation is used.  The amount of bedding below, above, and around the plastic pipe will vary depending upon trench conditions encountered and the amount of rock in the spoil that will be used as final backfill material.  At a minimum, 4 to 6 inches of bedding material is recommended.

- The Staff recommended that City Utilities continue their current practice of performing quarterly leak surveys of the downtown business areas.  Also, for plastic service lines that are beneath vent restrictive surfaces, the Staff recommended a complete FI survey over the service line and that a gas leak check be made near the service riser.  If no opening (e.g. 12” x 12” opening) exists in the asphalt or pavement near the service riser, a CGI reading performed in conjunction with a bar hole placed near the riser will need to be made.

- In reference to a list of plastic pipe leaks containing underground leaks from 1983-2003 in which the primary leak cause involved “aged/worn component”, “material failure”, “natural causes”, or “other”, the Staff recommended conducting spot-checks of these plastic mains to determine the pipe bedding condition near the pipe wall.  The spot checks should be made in two locations for each main approximately 20 feet (both directions) from the past repair area.  If rocks or other debris are found against the pipe wall, the plastic piping associated with that particular Job Order Number must be systematically replaced.

The list of plastic pipe leaks from 1983-2004, contains approximately 255 leaks on different plastic main segments and the Staff recommended that at least 20% or 51 of these leak locations be spot-checked annually for proper bedding material that is free from rocks or other materials that would make the piping susceptible to brittle-like failures.

##### In addition, as part of its continued investigation, the Staff requested that City Utilities provide quarterly assessments to address the following items.

- Results of the quarterly business district leak surveys of plastic piping, including piping beneath “vent-restrictive” surfaces.

- Leak repair records/Plastic Failure Reports of plastic pipe due to rock impingement.

- Plastic service line and main replacements to date.

- Schedules and records of training for personnel who are involved in documenting leak repairs of plastic pipe due to rock impingement, for personnel who are involved in determining backfill conditions during leak repairs of plastic pipe due to rock impingement, and personnel who are responsible for determining the extent of plastic piping that is an environment conducive to rock impingement when the piping is exposed for leak repair due to rock impingement.

The Staff believes that City Utilities has satisfactorily complied with all eight of Staff’s recommendations.  Information addressing the eight recommendations is outlined below.  Each of the numbers below corresponds with the numbers in Staff’s recommendations.

1.	City Utilities began tracking leaks due to rock impingement in 1998, and has since added some additional leak locations dating back to 1991, based upon information found during the investigation.  These prior leak locations have been compiled into a “Plastic Pipe Failure Master List.”  Since that time, this list has been the primary source for performing Gas Main Renewals in the City Utilities Gas System.

The Plastic Pipe Failure Master List currently contains 97 locations where a leak occurred due to rock impingement, and was subsequently repaired.  In 37 of the 97 locations, City Utilities replaced the piping that was installed under the same work order number for the main segment in question.  At each prior leak location, City Utilities has reviewed its record to determine the length of pipe that was installed under the work order number for the main segment number in question.  This method was chosen because it was felt that the length of pipe installed under the same work order number on a main segment would most likely have been installed using the same methods and in the same environmental conditions.

These sections of pipe will be included in a replacement program.   The remaining sections of pipe on the Plastic Pipe Failure Master List total 7.1 miles of piping yet to be replaced.  City Utilities will replace these sections over a three (3) year time, beginning August 16, 2004.  City Utilities has indicated that 861 associated service lines will also be replaced concurrently with these main replacements.

Any new segment of pipe (as described above) where a failure due to rock impingement is discovered will be replaced within a minimum of three (3) years from the date of its discovery.  Factors such as the number of leaks, operating pressure and environmental conditions shall be considered in the timing the replacement of the pipe.

- City Utilities’ current policy is to replace the gas service line from the main to meter if a leak due to rock impingement is found and verified.  There are 181 locations on the referenced list where only a portion of the service line where the leak occurred was replaced.  City Utilities will replace all of these services in their entirety from the main to the meter by December 31, 2005.

City Utilities has also agreed to replace the associated service line concurrently with any mains that have to be relocated due to other construction projects.

- City Utilities has modified their Plastic Pipe Failure Report form to include a specific category for “Rock Impingement” and a place for comments.  City Utilities has also developed written instructions to guide field employees in completing this form.  City Utilities’ field employees are currently using the new form.

- City Utilities conducted training regarding the proper way to complete this form for all affected employees on September 14, 2004.  Staff attended this training session.

- City Utilities has developed a Plastic Pipe Exposed Pipeline Condition Report form to document the backfill conditions surrounding the piping.  City Utilities has also developed instructions to guide field employees in completing this form each time a plastic pipe (main or service) is exposed.  City Utilities conducted training on the proper way to complete this form for all affected employees on September 14, 2004 (attended by Staff).  City Utilities field employees are currently using this new form.

If it is discovered that the backfill conditions surrounding the plastic piping contains rocks or other debris that could be detrimental to the piping, City Utilities will extend the excavation in both directions until suitable conditions are found.  If extending the excavation in both directions is impractical, an engineering evaluation will be performed to determine the appropriate remedial action.

- City Utilities has modified its Gas Construction Standards to require a minimum of 4 to 6 inches of bedding material around all newly installed plastic gas service lines that involve open trenches. This bedding material will typically be limestone sand.  City Utilities has proposed that other suitable materials or alternate protection methods such as rock shield sleeves may be evaluated and used in the future.

Staff’s review of City Utilities’ construction standards indicated that since at least 1977, their standards have contained specifications to use select dirt or AG limestone backfill in rocky areas during installation when directed by the Engineering Department.  The revised standard specifically requires the use of 4 inches to 6 inches of limestone bedding material around plastic pipe when being installed.

- City Utilities will continue its current practice of performing quarterly leak surveys of the downtown business areas.

City Utilities will perform an annual leak survey on the following items: the remaining segments of pipe contained on the “Plastic Pipe Failure Master List,” the services that were only partially replaced (until such time as they are renewed), and the segments where gas main leaks were repaired but were not verified to be due to rock impingement.

City Utilities, during routine FI leak surveys as required by the Missouri Pipeline Safety Regulations, will perform a bar-hole reading using a Combustible Gas Indicator (CGI) near the service riser where no opening exists around the riser for services located under vent restrictive surfaces.  City Utilities’ Operations and Maintenance Manual have been changed to reflect these procedures.

City Utilities has also conducted an instrument leak survey of all pre-1982 plastic gas piping in the first half of 2004.  During this survey, City Utilities treated all underground leaks on plastic piping as either a Class 1 or a Class 2 leak, giving them a higher priority than they may have otherwise had.  City Utilities will continue to classify all underground leaks on all plastic piping (mains and services) as either Class 1 or Class 2.

- City Utilities reports that of the 255 prior leak locations included on Staff’s list, 56 locations were duplicated on the Plastic Pipe Failure Master List and either have been or will be replaced. City Utilities will perform the recommended spot checks on the remaining 199 locations and will document the results.  City Utilities proposes that 33% (or 67 locations) be checked each year until all locations are checked.  Any locations that are found to have rocks or other debris against the pipe wall will be added to the list of plastic piping to be replaced as discussed under Item 1, above.

In addition, City Utilities has agreed to provide the Staff semi-annual reports as outlined below:

- Results of the quarterly business district leak survey.

- Results of leak surveys of plastic piping beneath vent restrictive surfaces.

- Results of annual leak surveys.

- The status of plastic service line and main replacements made to date.

- Schedules and records of training for personnel who are involved in documenting leak repairs of plastic pipe due to rock impingement, determining backfill conditions and who are responsible for determining the extent of plastic piping that is in an environment conducive to rock impingement.

In the Staff’s June 16, 2004 filing, the Staff recommended that City Utilities provide a “quarterly assessment” of the five items noted above.  After discussion with City Utilities, the Staff believes that a semi-annual report of these items, submitted to the Staff for review, will provide adequate monitoring and oversight of these activities.

SUMMARY

The Staff believes the recommendations contained in its June 16, 2004 report have been implemented into City Utilities’ gas safety program and are the foundation of City Utilities’ continuing plastic pipe replacement program.  All of these recommendations must be considered together in order to achieve the purpose of the replacement program, which is protection of the public’s safety, and each, therefore, complement the other. The Staff will continue to work with City Utilities to gather data to more clearly identify the plastic mains and service lines that require immediate attention and those that must be part of a longer term replacement program.

The Staff proposes to file an update report with the Commission on June 16, 2005.  This will allow Staff sufficient time to complete an analysis of the plastic pipe replacement program and leak survey data provided from City Utilities’ semi-annual reporting so Staff may provide the Commission with a comprehensive update report detailing the results of the plastic pipe replacement program and leak survey completed since Staff filed its investigative report on June 16, 2004.

Staff has been and will continue to monitor the effectiveness of City Utilities’ plastic main and service line replacement program and leak surveys.  If at any time, Staff determines that the program requirements should be enhanced, it will immediately bring its concerns and recommendations to the Commission.