Exhibit No.:

Issues:	Power Plant Decommissioning Costs

Witness:  	Thomas S. LaGuardia

Sponsoring Party:	Union Electric

Type of Exhibit: 	Rebuttal Testimony

Case No.:	EC-2002-1

Date Testimony Prepared:	May 10, 2002

MISSOURI PUBLIC SERVICE COMMISSION

CASE NO. EC-2002-1

REBUTTAL TESTIMONY

OF

THOMAS S. LAGUARDIA

ON

BEHALF OF

UNION ELECTRIC COMPANY

d/b/a AmerenUE

St. Louis, Missouri

May, 2002

Table of Contents

Page

- QUALIFICATIONS	1

## II.	EXPERIENCE	2

III.	PURPOSE AND SCOPE	8

IV.	METHODOLOGY	11

- CONTINGENCY	21

- DISMANTLING	24

- SALVAGE AND SCRAP	27

- DISMANTLING FEASIBILITY	27

- REGULATORY APPROVAL OF DECOMMISSIONING	27

REBUTTAL TESTIMONY

OF

THOMAS S. LAGUARDIA

CASE NO. EC-2002-1

### I.	QUALIFICATIONS

Q.	Please state your name and business address.

A.	My name is Thomas S. LaGuardia.  My business address is 148 New Milford Road East, Bridgewater, CT  06752.

Q.	What is your occupation?

A. 	I am President of TLG Services, Inc. (TLG), a subsidiary of Entergy Nuclear, Inc. (ENI).

Q.	What are your responsibilities with TLG?

A.	I am responsible for the technical and business management of engineering and field services in the areas of decontamination, decommissioning, waste management and general engineering for nuclear and fossil-fueled electric generating stations.

Q.	What is your educational and professional background?

A.	I completed my Bachelor of Science in Mechanical Engineering at Polytechnic Institute of Brooklyn in 1962, and my Master of Science in Mechanical Engineering at the University of Connecticut in 1968.  I am a registered Professional Engineer in Connecticut (No. 10393), New York (No. 059389), New Jersey (No. 38193), and Virginia (No. 033747).  I am a Board Certified Cost Engineer by the Association of the Advancement of Cost Engineering (AACE No. 1679).  I founded TLG Engineering in April, 1982 and TLG Services in January 1994.  I sold TLG Services to ENI in September 2000 and was retained as President of TLG Services and VP of Decommissioning for ENI.

I was employed by Nuclear Energy Services in Danbury, Connecticut, from 1973 until I founded TLG Engineering.  My prior employment was with Gulf Nuclear Fuels Corporation, formerly United Nuclear Corporation (UNC), and Combustion Engineering.

## II.	EXPERIENCE

Q.	Do you have experience in the design and construction of fossil-fueled generating stations?

A.	Yes.  During my employment with Combustion Engineering, Inc. from 1962 to 1968, I was a boiler design, performance and construction engineer for 500 megawatt electric (MWe) coal-fired power boilers and merchant and Naval oil-fired marine boilers.

Q.	What decommissioning experience do you have?

A.	My decommissioning experience began as site representative for UNC during the BONUS reactor decommissioning in 1969 and 1970.  BONUS was a 17 MWe demonstration power reactor located in Puerto Rico that was owned by the U.S. Atomic Energy Commission (USAEC), now the U.S. Department of Energy (USDOE), and operated by the Puerto Rico Water Resources Authority.  It was the largest reactor decommissioned by entombment up to that time.  The program involved extensive chemical decontamination of radioactive systems, selective piping and component removal, and entombment of the reactor vessel within a massive concrete barrier.  The entombment has a design life of 125 years.  My role as site representative was to act as a technical liaison and provide project engineering and schedule management assistance during system decontamination, component removal, vessel entombment and facility close-out.

Following the BONUS program, I was lead engineer for UNC during the Elk River Reactor decommissioning between 1970 - 1973.  Elk River was a 20 MWe demonstration power reactor located in the state of Minnesota that was owned by the USAEC and operated by United Power Association.  Elk River was decommissioned by complete dismantling.  The program involved segmentation of the reactor vessel and internal components using remotely-operated cutting torches, as well as the packaging, shipping and controlled burial of the segments.  Similarly, radioactive piping and components were removed, packaged, shipped and buried.  Radioactive concrete was demolished by controlled blasting, and nonradioactive concrete was demolished by wrecking ball to completely dismantle the facility.  Initially, my role for UNC was Consulting Engineer and later Lead Engineer for UNC technical support for on-site activities.

I was Project Engineer, while at Nuclear Energy Services, for the detailed engineering and planning of the Shippingport Station Decommissioning Project from 1979 - 1982.  Shippingport was a 72 MWe light water breeder reactor located in the state of Pennsylvania, owned by the USDOE and operated by Duquesne Light Company.  The facility is now dismantled, and TLG with its joint venture partner, Cleveland Wrecking Company, dismantled all of the clean and contaminated piping and components and removed contaminated concrete.  My role for TLG/Cleveland was Project Director, and I selected and managed an on-site project management team to hire and supervise work crews to accomplish the dismantling.  All work was completed on schedule and within budget.

I also assisted Atomic Energy of Canada, Ltd. in the detailed engineering and planning for the decommissioning of the 238 MWe Gentilly Unit 1 reactor located in Three Rivers, Canada.  My role was to provide overall decommissioning consulting services and detailed cost estimation of alternatives.

TLG worked with the Northern States Power Company between 1988-89 in the preparation of the decommissioning plan for the Pathfinder Atomic Power Plant.  Pathfinder, located in Sioux Falls, S.D., was a 60 MWe reactor initially placed in a safe storage condition (SAFSTOR) after an abbreviated operating life.  TLG prepared detailed cost and schedule estimates and vessel activation estimates, analyzed the reactor vessel to be used as its own shipping container, and prepared the decommissioning plan in support of plant decommissioning.

TLG has also assisted the Sacramento Municipal Utility District since 1989 with the decommissioning planning for the Rancho Seco Nuclear Generating Station.  This work included a detailed reactor vessel activation analysis, preparation of decommissioning alternative cost and schedule estimates, and assistance with the preparation of the decommissioning plan originally using the SAFSTOR method and more recently reflecting the DECON method.

TLG worked with the Long Island Lighting Company in the planning for the decommissioning of the Shoreham Nuclear Power Station.  This work included the preparation of a detailed reactor vessel activation analysis, cost estimates, schedules, management organization, waste volume estimates and draft decommissioning plan.

In 1990, TLG was selected by Cintichem, Inc. (a subsidiary of Hoffman-LaRoche) as Decommissioning Co-Manager of a 10 megawatt thermal (MWt) research reactor and associated hot cells and facilities.  TLG's staff prepared a reactor core activation analysis as well as cost and schedule estimates for the project.  TLG assisted in the preparation of the decommissioning plan, which was approved by the NRC.  TLG's field management staff was on-site co-managing the project with the Cintichem staff and supervising the work crews in decommissioning and dismantling the facility. The program is complete.  My role in the project was Senior Decontamination and Decommissioning Expert on the Nuclear Safeguards Committee.

TLG has also been involved in the engineering and planning activities associated with the decommissioning of the Yankee Rowe, Trojan and Big Rock Point, Humboldt Bay 3, Maine Yankee and Oyster Creek nuclear units.  This work includes activation analyses, preparation of decommissioning alternative cost and schedule estimates, and assistance with the preparation of the decommissioning plans.  In addition, TLG was selected to prepare the steam generators and the pressurizer at Trojan for transport to the burial facility at Richland, WA.  TLG was responsible for certifying package integrity, overseeing the grouting of the components and preparing any supporting transportation analyses.  The project was successfully completed in October 1995.  TLG supported Portland General Electric (PGE) in the detailed planning required for completing the decontamination and dismantling of the Trojan nuclear unit, including the intact removal and disposal of the reactor vessel and the highly radioactive internal components.

In addition, TLG prepared the Decommissioning Plan for Dresden Unit 1 and the Environmental Reports (ER) for Dresden Unit 1 and Indian Point Unit 1.  Under my supervision and direction, TLG has prepared site-specific decommissioning studies for approximately 85% of the nuclear units in the United States

TLG was recently awarded a contract to demolish the contaminated concrete in the containment building of the Saxton Nuclear Power Plant.  Saxton was a 60 Mwe experimental facility and is located in Saxton, PA.

I was a past member of the Executive Committee of the Decommissioning, Decontamination and Reutilization Division of the American Nuclear Society.

Q.	What dismantling experience do you have on fossil-fueled plants?

A.	TLG was responsible for overseeing the dismantling and demolition of a fossil-fueled steam plant for a major Connecticut hospital facility.  In connection with this demolition project, I participated in the site inspection and cost estimate development.  The work was subcontracted and TLG personnel supervised the contractors.

TLG supervised the dismantling of the Comal fossil-fueled power plant (containing four boilers) in New Braunfels, TX.  The power plant equipment was removed for scrap, and the boiler building restored as a local landmark.

TLG is also participating in dismantling of the Seaholm Power Plant (containing five boilers) in Austin, TX.  The boiler and power plant equipment will be removed, and the building restored as a local landmark.

TLG has prepared site-specific dismantling studies for approximately 200 fossil-fueled power generating units.

Q.	Have you prepared or co-authored any studies and reports on decommissioning and dismantling cost estimating and technology?

A.	Yes.  While at Nuclear Energy Services, I was Principal Investigator for the Atomic Industrial Forum’s National Environmental Studies Project (NESP) decommissioning study entitled “An Engineering Evaluation of Nuclear Power Reactor Decommissioning Alternatives” (AIF/NESP-009).  The Atomic Industrial Forum (now Nuclear Energy Institute) is an industry supported advocate and sponsor of research to promote the advancement of nuclear power.  This study evaluated the costs, schedules and environmental impacts of decommissioning 1100 MWe reactors (Pressurized Water Reactors [PWRs], Boiling Water Reactors [BWRs], and High Temperature Gas-Cooled Reactors [HTGRs]).

I also co-authored the “Decommissioning Handbook” for the USDOE.  The Handbook reported the state-of-the-art in decommissioning technology (as of 1980), including decontamination, piping and component removal, vessel segmentation, concrete demolition, cost estimating and environmental impacts.

At TLG Engineering, in 1986, I co-authored “Guidelines for Producing Commercial Nuclear Power Plant Decommissioning Cost Estimates” (AIF/NESP-036) for the Atomic Industrial Forum’s National Environmental Studies Project.  The Guidelines identify the elements of costs to be included in the estimation of decommissioning activities for each of the principal decommissioning alternatives. Specific guidance in cost estimating methodology and reference cost data is provided in this study.  The major objective of this study is to provide a basis for consistent cost estimating methodology.

In 1986, TLG Engineering also prepared a study for the NRC, which I co-authored, entitled, “Identification and Evaluation of Facilitation Techniques for Decommissioning Light Water Power Reactors” (published as an NRC contractor report - NUREG/CR-3587).  The study evaluated the costs and benefits of techniques to reduce occupational exposure and waste volume from decommissioning.

TLG personnel also authored the paper “How to Determine the Cost of Dismantling a Fossil-Fuel Electric Power Plant” (A. Carlstrom, Cost Engineering Magazine, April, 1989).

I am currently an editor and author (with other authors including TLG personnel) of a new U.S. DOE Decontamination and Decommissioning Handbook to be published by the ASME in 2002.

III.	PURPOSE AND SCOPE

Q.	What is the purpose of your testimony in this proceeding?

A.	I am presenting the results of a dismantling cost study prepared by TLG as shown in Schedule 1, for the following Ameren fossil-fueled power plants:

###### SUMMARY OF DISMANTLING COST ESTIMATES

| Station | No. of Units | Megawatts (total) | Dismantling Cost (millions) |
| --- | --- | --- | --- |
| Labadie | 4 | 2520 | $112.9 |
| Rush Island | 2 | 1260 | $65.7 |
| Sioux | 2 | 59.5 | $59.5 |
| Meramec | 4 | 940 | $60.2 |

- Do the costs shown in the Summary table include the cost of removal of asbestos insulation on piping and components?

A.   The costs listed in the Summary table assume removal of the asbestos insulation at the Venice Plant only.  Following the completion of the study, TLG performed additional studies to estimate the cost to remove asbestos insulation from piping and components at the other four plants.  These additional costs are shown in the following table for each power plant site.  Because the dismantling cost estimates shown in the table below are not included in the study, the dismantling costs estimated by the study are conservative.

ASBESTOS REMOVAL COST

| Station | Asbestos Removal Cost (millions) |
| --- | --- |
| Labadie | $15,544 |
| Rush Island | $2,135 |
| Sioux | $10,018 |
| Meramec | $9,133 |
| Venice | $1,514 |

Q.	What is covered by the term “retirement” as used with reference to a fossil-fired generating station?

A.	Retirement is the planned and orderly removal from service of a generating station.  Upon retirement, the facility may either be rendered safe indefinitely (through on-going monitoring, maintenance, repair and security measures), or dismantled.

Q.	Please summarize the costs identified in the dismantling study.

A.	Dismantling and demolition of the Labadie, Rush Island, Sioux, Meramec and Venice fossil-fired steam electric generating stations was estimated to cost approximately $337.6 million total (2001 dollars), including credit for the scrap generated in the dismantling process.  Each site was assumed to be dismantled upon the cessation of the final unit’s operation.

Q.	Was the dismantling study, prepared for Ameren, prepared under your direction and supervision?

A.	Yes.  I developed the basic methodology used by TLG to estimate the costs to dismantle fossil-fueled power plants.  I trained my engineering and estimating staff in this methodology.

During the preparation of the study, I provided guidance and interpretation to the TLG staff on how to estimate specific elements of cost.  I visited each of the plants t familiarize myself with the plants designs and site-specific issues to be addressed in the study.  I reviewed the results of the estimate to ensure the results were reasonable and representative of the features of the plant.  Finally, I supervised the preparation of the report summarizing the results of the estimate.

IV.	METHODOLOGY

Q.      What procedure was used for developing the dismantling cost study for the Ameren power stations?

- The  study was developed using site plans and data sheets, together with plant descriptions for the Ameren power stations.  The TLG estimating staff visited each of the plants to familiarize themselves with the units.  The Ameren power plants were compared to other similar fossil power plants with detailed dismantling cost estimates prepared by TLG.  The dismantling costs were developed by ratio of specific power plant parameters such as equipment inventory, structural components, and size of major components (turbine-generators, feedwater heaters, etc.).  The ratioed costs of each component were then summed to arrive at the dismantling cost estimates for the Ameren power stations.

Q.	What accuracy do you ascribe to the Ameren dismantling estimates as developed by TLG?

A.	The Association for the Advancement of Cost Engineering (AACE) defines three levels of estimates in its Cost Engineer's Notebook.  An "order-of-magnitude" estimate is appropriate for conceptual studies, or where detailed information is not readily available to determine a site-specific estimate.  Such estimates are expected to have an accuracy of between -30% and +50%.  A "budgetary" estimate is appropriate where detailed information is available to compare the current or proposed design to a similar design, and direct or ratioed comparisons can be made.  Budgetary estimates are expected to have an accuracy of between  -15% to +30 %.  A "definitive" estimate is appropriate for detailed studies when all the parameters and/or final designs are completed to determine a site-specific estimate.  Definitive estimates are expected to have an accuracy of between -5% to +15%.

The Ameren stations estimates would qualify as a "budgetary" estimate with an expected accuracy of -15 to +30%.  The "other" estimates relied upon by TLG to develop the Ameren estimates were site-specific estimates, and would therefore be categorized as definitive estimates with an expected accuracy of -5% to +15%.

Q.	What type of costs are analyzed in a dismantling study?

A.	There are three types of costs included and analyzed in a dismantling study: activity-dependent costs, period-dependent costs and collateral costs.  Activity-dependent costs are those associated with the physical work of removing piping, components and structures and transporting and disposing of the same.  These costs represent labor, materials and special services (subcontracted) costs associated with the work crew’s activities (hence, activity-dependent costs).  The summation of the durations to perform these activities when properly sequenced provides the overall schedule for the project.

Period-dependent costs are those associated with the management staff costs which are necessary to provide technical and administrative direction to the project.  These management costs must continue for the duration of the project.  The project is divided into three periods:  1)  Asbestos Abatement and Engineering/Planning; 2) Dismantling Operations; and 3) Site Restoration.  The management staff size is adjusted to reflect the crew size and work activities in each period.  Accordingly, these staff costs are period-dependent.

Collateral costs are all those costs which are neither activity- nor period-dependent.  They include insurance, large equipment rentals and special tools, plant energy, etc.

Q.	What methodology was used to prepare other similar fossil power plant detailed cost estimates?

A.	The methodology used to develop the other detailed cost estimates followed the basic approach presented in the AIF/NESP-036 study report, “Guidelines for Producing Commercial Nuclear Power Plant Decommissioning Cost Estimates,” the USDOE “Decommissioning Handbook”, and American Association of Cost Estimators paper “A  Methodology for Determining the Cost of Dismantling Fossil-Fueled Electric Power Plants.”  Obviously, nuclear power plant concerns are not necessary for fossil power plants and, therefore, none were included in the study.  However, the basic methodology, which is widely accepted by the electric power industry and regulatory commissions throughout the United States, is applicable for fossil plants as well.

Q.	How was this methodology applied to the other similar fossil plant cost estimates?

A.	The aforementioned references use a unit cost factor method for estimating decommissioning activity costs to standardize the estimating calculations.  Unit cost factors for activities such as concrete removal ($/cu yd), steel removal ($/ton), and cutting costs ($/in.) were developed based on the labor cost information provided.  Consumable material and equipment rental costs (crane and truck rental, operating costs for heavy equipment, torch cutting gas consumption, etc.) were taken in large part from R.S. Means, “Building Construction Cost Data 2001.”  The activity-dependent cost for removal, shipping and disposal were estimated using the item quantity (cu yds, tons, inches, etc.) developed from plant drawings and inventory documents.  The activity duration critical path derived from such key activities as boiler removal, turbine removal etc., was used to determine the total dismantling program schedule.

The program schedule is used to determine the period-dependent costs such as program management, administration, field engineering, equipment rental, and security.  The salary and hourly rates are typical for personnel associated with period-dependent costs.

In addition, collateral costs were included for heavy equipment rental or purchase, safety equipment and supplies, energy costs, permits, and insurance.

The activity-dependent, period-dependent, and collateral costs were added to develop the total dismantling costs.  As discussed later, a contingency percentage was added to allow for the effect of unpredictable program problems on costs.  Such a contingency is appropriate for a project of this size and type.  The total dismantling costs plus contingency, less scrap credit provides the total project cost.  One of the primary objectives of every dismantling program is to protect public health and safety.  The cost estimate for the dismantling activities includes the necessary planning, engineering and implementation to provide this protection to the public.

Q.	For purposes of the estimate, when did you assume the units at each site would be dismantled?

A.	We assumed dismantling of each unit would occur upon retirement of the last unit at each site.  This approach is reasonable because it would be more difficult and costly to protect the operating units from potential damage when demolishing the retired units.  Moreover, the dismantling staff and crew would only have to mobilize and demobilize once for the site instead of each time a unit is retired.  Using the same staff and crew would take maximum advantage of the lessons learned as the units are dismantled in sequence.

Q.	What are the major differences between nuclear and fossil power plants?

A.	The major difference is the radioactivity contained in nuclear power plants.  Removal of radioactively contaminated piping, components and structures from a nuclear plant is more difficult and costly than the removal of comparable items from a fossil plant.  The activities of decontaminating, removing, packaging, shipping and burying radioactive materials from a nuclear plant require strict radiological controls, special containments and packaging, and licenses for the transport for disposal.  There are many more opportunities for problems to arise in nuclear plant decommissioning than in fossil plant dismantling.

Fossil plants have no radioactivity, but they may contain asbestos, polychlorinated byphenals (PCBs), mercury (in switches), lead, and other hazardous materials.  These materials require special handling and disposal, but in general, productivity is higher overall when fossil plants are dismantled than when nuclear plants are decommissioned, and the overall cost is lower.

Q.	Does your experience in the decommissioning of nuclear power plants aid in the conduct of a site-specific dismantling study of a fossil-fueled power plant?

A.	Yes.  The parallelism in approach between nuclear plant decommissioning and fossil plant dismantling enables us to rely on the field experience from nuclear decommissioning to prepare fossil plant studies.  In particular, the following major areas of planning and estimating exhibit similar characteristics.

1.	Site Characterization

The process and planning for identification of radionuclide contamination composition and extent for nuclear power plants is similar to that required for potentially hazardous materials in fossil-fueled power plants.

2.	Removal of Hazardous Material (Asbestos)

Planning and removal of asbestos-containing materials in nuclear and fossil plants is identical.

3.	Sequencing of Work Activities

Identification and sequencing of essential (to the decommissioning task) and non-essential systems removal follows the same considerations in both types of plants.  Essential systems include electric power, lighting, and service water systems.  For example, power and lighting would be retained as long as possible to assist in the dismantling process.

4.	Management Staff

Identification of utility and decommissioning (dismantling) staffing composition and levels follows the same process in both types of units.  The specific job functions will differ but the logic is the same.  Management staff costs are period-dependent; that is, they are a function of the overall project duration.

5.	Removal of Non-Contaminated Equipment/Structures

Removal of non-contaminated piping, components and structures are activity-dependent.  The methods for their removal are identical for most of the systems and structures in each type of plant.  Piping diameters and lengths are similar (size-for-size plants), and the removal rate will be the same.  Clean components, such as feedwater heaters and pumps, condensate pumps, demineralizer systems, etc., in nuclear plants, are the same sizes and types as those found in fossil plants.  Steel and concrete structures are removed in the same manner in both types of plants.  Removal of equipment unique to fossil plants, such as coal handling and air/flue gas duct systems, relates to the weight of sub-components, and is accomplished by rigging and segmentation.

6.	Scheduling

The scheduling of work activities for either type of plant follows the proven planning techniques of activity precedence networks and critical path management.  An activity precedence network consists of a series of sequenced activities based upon the priority or “precedence” of completing one or more activities before starting another activity.  The critical path is the longest sequence of work activities in a precedence network from project initiation to completion.

7.	Collateral Cost

Collateral costs are neither activity-dependent nor period-dependent costs.  These items are identical in both types of plants, although specific cost values will differ.

8.	Contingency

Contingency, as described more completely later in this testimony, is a cost allowance for field-related problems that are likely to occur.  These problems include tool and equipment breakdown, late deliveries of supplies and equipment, and adverse weather.  These field problems occur in both nuclear and fossil plant dismantling, although the specific allowances differ in each case.

9.	Field Experience

The field experience in both nuclear and fossil plant dismantling for clean equipment is essentially identical.  Heavy lifts of components weighing 50 to 450 tons are common in both plant types, and the planning and implementation activities are virtually identical.

In summary, the nuclear plant decommissioning experience is directly applicable to fossil plant dismantling.

Q.	How does this estimating process differ from construction estimating?

A.	There is very little difference in the elements of cost between fossil plant dismantling and construction.  Both activities must account for labor, materials, equipment, services and collateral costs (as defined earlier).  The activities related to construction are similar to those for dismantling.  Specifically, construction activities such as rigging components into position and welding connecting piping are comparable to dismantling activities such as cutting connecting piping and rigging components out of the structures.  In the case of construction however, the pipe welds must be inspected and re-welded if flaws in the weld are identified.  This re-work causes schedule delays and incurs additional expense.  In the case of dismantling, the pipe need only be cut once.  Problems in dismantling occur when plant drawings and specifications do not properly reflect the plant as constructed.  This occurs when changes to the plant are made that have not been recorded on the as-built drawings.  This can result in additional dismantling costs.  However, in general, dismantling cost estimating is comparable to construction cost estimating.

Q.	Please describe the process of dismantling a fossil power plant.

A.	Approximately three months prior to final shutdown, engineering and planning would begin on the preparation of the Dismantling Engineering Plan (Plan) and Environmental Report (ER).  The Plan describes the status of the facility at shutdown, work to be accomplished, safety analyses associated with each of the major activities, general procedures and sequence to be followed, and final site condition upon completion of all work.  Similarly, the ER would evaluate environmental effects to workers and the public, and waste generation effects on the site and environment.  These documents would be submitted to the Environmental Protection Agency and other applicable regulatory agencies for review and approval, and authorization to proceed.

The sequence of work would be as follows:

Period 1 - Site Preparations - would begin upon shutdown of the facility, and would involve site preparations to initiate dismantling.  All usable fuel is assumed to have been burned or removed prior to shutdown.  Asbestos abatement work is completed.

Period 2 - Dismantling Operations - would begin upon receipt of approval of all regulatory agencies.  This phase of the work involves the removal of all components of the boiler, air quality treatment systems (electrostatic precipitators, etc.), fuel handling systems (coal conveyors, crushers, oil storage tanks, etc.), the turbine-generator, condensate and feedwater systems.  In general, the boiler will be dismantled in a bottoms-up mode, whereby the lower sections of the boilers will be cut at grade level, and remaining upper sections lowered to grade or scaffolding erected to cut the upper sections of the boiler furnace.  This method of dismantling is necessary for the top-hung type of boiler that is supported from the steel structure.

Care must be taken to ensure boiler sections are removed uniformly from the bottom up to avoid any unbalanced load on the steel structure that may cause it to become unstable.

Steel structures used to support the boiler and turbine-generator components will be dismantled by controlled demolition (by lowering sections to grade by cranes) to prevent injury to workers on lower floors.  The steel structures will be dismantled from the top down, essentially reversing the construction sequence.

Concrete structures such as boiler foundations, floors, turbine-generator pedestals and support buildings will be demolished by conventional wrecking methods.  These may include the use of wrecking balls, pneumatically-operated rams on a backhoe, or controlled blasting.

Period 3 - Site Restoration - would involve the re-grading of all areas that were disturbed by the dismantling process.  All structures will be removed to three feet below grade to permit re-vegetation of the site, or to eliminate at-grade hazards.  Clean rubble would be used on site for fill and additional soil would be used to cover each subgrade structure.  The site would be graded.

Q.	Is it possible that future changes in technology and regulation could affect the dismantling costs?

A.	Yes.  The TLG cost estimates prepared for these plants are based on state-of-the-art technology.  No provision is made to adjust for cost changes associated with future changes in technology and regulations.  It is my recommendation that Ameren thoroughly review these estimates periodically and revise them, if necessary, to account for cost increases or decreases as influenced by future technology and regulations, OSHA requirements, environmental concerns, etc., and general inflation as measured by the Consumer Price Index.

V.	CONTINGENCY

Q.	What Is The Basis For The Contingency?

A.	The purpose of the contingency is to allow for the costs of high probability program problems, where the occurrence, duration, and severity cannot be accurately predicted and have not been included in the basic estimate.  The inclusion of contingency in cost estimation for both construction and dismantling is well accepted.  The American Association of Cost Engineers (AACE) (in their Cost Engineer’s Notebook) defines contingency as follows:

Contingency - specific provision for unforeseeable elements of cost within the defined project scope; particularly important where previous experience relating estimates and actual costs has shown that unforeseeable events which will increase costs are likely to occur.

Past dismantling and decommissioning experience has shown that these problems are likely to occur and may have a cumulative impact.

Fossil-fueled and nuclear power plants share some of the same potential problems leading to the need for contingency in cost estimates.  These problem areas include:

- Schedule slippages - leading to crew overtime payments and/or project extensions

- Weather delays - loss of productivity, overtime, slippages

- Labor strikes - loss of productivity, slippages

- Workers injuries -	production interruptions, additional safety training, workers compensation claims, possible increased insurance premiums

- Material shipping - rescheduling of activities, inefficiencies in production,

- Equipment breakdowns -	rescheduling of activities,  out-of-scope backcharges from subcontractors

- Regulatory inspections - insurance inspectors, Occupational Safety and Health Act (OSHA) inspectors, federal and state EPA inspectors, state building inspectors

- Hazardous materials - special handling requirements beyond planned requirements

A more extensive discussion of nuclear contingency is included in the AIF/NESP-036 Guidelines Study (Chapter 13) referred to earlier.  In that study, contingencies for the individual activities ranged from 10% to 75%, depending on the degree of difficulty judged to be appropriate from our actual decommissioning experience.  The overall contingency, when applied to the appropriate components of nuclear plant decommissioning costs, results in an average contingency of up to 25%.

For fossil plant dismantling, the absence of radioactive materials and their attendant potential problems simplifies the dismantling process.  Individual activity contingency estimates for fossil-fueled power plants usually use factors in the range of 15% for work involving non-hazardous materials and 25% for work involving hazardous materials.

Independent of our preparation of this estimate for Ameren, R.S. Means, “Building Construction Cost Data 2001,” suggests that a 15% contingency factor for conventional construction be used.

Q.	How do the contingency factors developed for the Ameren estimate compare to contingency factors adopted by regulatory agencies for nuclear plant decommissioning?

A.	As I discussed earlier, the nuclear contingency is generally in the range of 20-25%.  The Federal Energy Regulatory Commission (FERC) adopted a 25% contingency for nuclear power plant decommissioning as reasonable.  Numerous state public utility commissions have adopted a 25% contingency for nuclear plant decommissioning, as evidenced by an American Gas Association-Edison Electric Institute Depreciation Committee Survey, which showed that at least 21 of 32 utility survey respondents had included a 25% contingency in their estimates.  The survey also showed that of the 15 utilities who filed rate cases, 11 had approval to use the 25% contingency for their plant decommissioning studies.

Q.	Have you compared estimates and actual costs for decommissioning projects that have been undertaken to date.

A.	Yes.  Based upon information available, TLG’s estimates for recent work performed are on average within 4% of the actual costs reported (including contingency).

Q.	Is the variation between estimated and actual costs due to contingency costs?

A.	No.  The differentials were either the result of modifications in the management of the intended program or savings in disposal costs negotiated by the licensee with the burial facility during the project.  Since the contingency, as applied in the TLG’s estimates, is not pricing or scope related, the correlation of estimated and actual project costs validates the need for contingency in decommissioning planning.

VI.	DISMANTLING

Q.	Why is dismantling after a power plant is taken out of service the appropriate alternative?

A.	Securing, maintaining and guarding retired power plants indefinitely is costly, which will require either a full-time guard force, and/or intrusion detection devices and alarms monitored by local law enforcement agencies, as well as general building maintenance to keep the structures in a safe condition.  Furthermore, prompt dismantling of retired power plants makes the site available for alternative uses at the earliest possible time.

Q.	Is reuse of the site for a power plant a possibility?

A.	Yes.

Q.	If the site could be reused, why couldn’t the power plant components be reused in repowering?

A.	The designs of new generation power plants are not likely to use the same size and configuration of components, nor require the same type of building enclosures.  Optimum facility design will be sized to match the megawatt size of a replacement power plant, if any, either larger or smaller.  For example, new combustion turbine-generators are modular, self-contained units that don’t need a building enclosure.  Combined cycle units may require larger turbine buildings to enclose the waste heat steam generators which supply steam to the turbine.  The cost to renovate older buildings and bring them to current safety code standards, combined with the less-than-optimum facility design makes reuse of the existing powerhouse buildings an unlikely scenario.  Furthermore, the existing components are likely to be of an obsolete design, more costly to operate and maintain, and may not be compatible with new instrumentation and control systems.

Q.	Why is it necessary to dismantle a fossil-fired plant?

A.	Remediation of fossil-fired facilities is inherently destructive, and may include creation of large access ways, dismantling of peripheral structures, concrete demolition including controlled blasting, removal of roofs and walls, excavation of footings, etc.  Precluding reconstruction, a retired fossil-fired facility poses hazards including large interior open areas, pits, shafts and underground tunnels.  With many of the plant services removed from service, the structures would be dark, littered with concrete rubble and structural debris obstructing means of egress.  Condensation and groundwater intrusion, and bird infiltration would soon create hazardous conditions, promoting unsanitary biological infestations, accelerating corrosion, and general facility deterioration.  A dedicated and systematic maintenance program is necessary to maintain the facility in a “safe” condition.  Security measures are necessary to limit the liability inherent in casual or deliberate intrusion by the public.  These maintenance and surveillance programs are expensive.

The steel and concrete or brick structures at fossil sites were not designed to prevent deliberate intrusion.  Large glass windows, sheet metal siding, loading ramps and multiple ingress points allow easy entry into the station confines.  Visitation of older, shutdown units has conclusively demonstrated both the speed and effects of facility deterioration.  Such deterioration includes broken windows, leaking roofs, torn or damaged siding, obstructed stairwells with poor egress, and unsanitary conditions caused by the effects of weather, corrosion, ground water intrusion and vermin.  Stacks, mine openings, fill ponds and lagoons with steep sloped banks, and river intake structures are high exposure liabilities and inherently dangerous to human life.

The alternative to perpetual caretaking and site surveillance is to dismantle the site as soon as practical.  This activity is the most cost-effective when included within the schedule for site remediation, due to resources available on-site and the expected condition of the facilities.

Q.	Can you cite some examples where fossil-fueled power plant were dismantled?

A.	Yes.  As I mentioned in the Experience section of my testimony, the Comal and the Seaholm plants in Texas were dismantled although the buildings were retained as local landmarks.  These plants were built in the early 1900s and were no longer economical to operate.

In Missouri, Kansas City Power & Light retired and dismantled the Northeast Station located in Kansas City.  This plant was built and placed in service in 1945, and was dismantled in 1985, after about 40 years of operation.  The plant capacity was replaced with the Callaway and Wolf Creek nuclear power plants, and was no longer needed.

VII.	SALVAGE AND SCRAP

Q.	How was scrap or salvage credit included in the overall estimate?

A.	Credit for carbon steel, stainless steel and copper scrap is included in fossil plant estimates based on published scrap values.  No credit was included for salvage of any components because these components will be of an obsolete design by the time these plants are dismantled.  As such, these materials were considered as scrap.

VIII.	DISMANTLING FEASIBILITY

Q.	What is the feasibility of the dismantling premise?

A.	There is extensive experience in the United States and in other countries for the complete dismantling of fossil power plants and related industrial facilities.  This experience includes the dismantling of chemical refineries, steel mills, and nuclear power plants (with their associated non-nuclear turbine-generator portions).  This directly related experience shows that the Ameren power plants can be completely dismantled safely.

# IX.  REGULATORY APPROVAL OF DECOMMISSIONING

Q.	Has the Missouri Public Service Commission approved decommissioning estimates?

A.	Yes.  The Missouri Public Service Commission has accepted TLG’s cost estimates for decommissioning the Callaway and Wolf Creek nuclear plants.  These estimates include dismantling of the decommissioned structures, following license termination at nuclear power plants, and are an appropriate measure to protect public health and safety.  The same safety concerns exist at retired fossil-fired power stations, and for this reason TLG recommends dismantling fossil-fired power plant structures.

Q.	Have other regulatory agencies approved fossil-fired power station dismantling cost estimates?

A.	Yes.  I am aware that the Florida Public Service Commission in its Order No. 24741 in Docket no. 890186-EI, approved dismantlement studies and associated costs for fossil-fired units as filed by Gulf Power Company, Tampa Electric Company, Florida Power Corporation and Florida Power & Light Company.

Q.	Does this conclude your testimony?

A.	Yes it does.

##### BEFORE THE PUBLIC SERVICE COMMISSION

OF THE STATE OF MISSOURI

The Staff of the Missouri Public Service 	)

Commission,					)

Complainant,		)

)

vs.						)	Case No. EC-2002-1

)

Union Electric Company, d/b/a		)

AmerenUE,					)

Respondent.		)

AFFIDAVIT OF THOMAS S. LAGUARDIA

STATE OF CONNECTICUT 	)

) ss

CITY OF BRIDGEWATER		)

Thomas S. LaGuardia, being first duly sworn on his oath, states:

1.	My name is Thomas S. LaGuardia.  I am President of TLG Services, Inc. (TLG), a subsidiary of Entergy Nuclear, Inc. (ENI) in Bridgewater, Connecticut.

- Attached hereto and made a part hereof for all purposes is my Rebuttal Testimony on behalf of Union Electric Company d/b/a AmerenUE consisting of ___ pages, Appendix A and Schedules __ through ___, all of which have been prepared in written form for introduction into evidence in the above-referenced docket.

3.	I hereby swear and affirm that my answers contained in the attached testimony to the questions therein propounded are true and correct.

________________________________________

Thomas S. LaGuardia

Subscribed and sworn to before me this ____ day of May, 2002.

________________________________________

Notary Public

My commission expires: